# Transformer Inspection Report — XFMR-00040

Asset inspection record for transformer XFMR-00040, a 43.02 MVA unit manufactured by ABB and installed in 2002 (24 years in service). The unit is connected to feeder feeder-049-0003 at substation sub-samuelhaven-049 and its current status is in_service.

Visual inspection findings: oil level and condition — slight discoloration, within spec. Bushings — no visible tracking. Cooling fans and radiators were cycling correctly under load. Grounding connections were verified intact. Inspection performed by a Substation Technician under weather conditions: thunderstorms.

SCADA alarm history for XFMR-00040 over the trailing twelve months shows 3 recorded alarms: differential protection trip (1), ground fault (1), overcurrent (1). 1 of these remain unresolved.

Thermal alarm count (1) is below the capacity-upgrade-review threshold. No loading study is required at this time.

Recommended follow-up: no action required; return to standard inspection rotation.