# Transformer Inspection Report — XFMR-00074

Asset inspection record for transformer XFMR-00074, a 56.13 MVA unit manufactured by GE Vernova and installed in 1990 (36 years in service). The unit is connected to feeder feeder-050-0448 at substation sub-martinezbury-050 and its current status is in_service.

Visual inspection findings: oil level and condition — darkened — schedule dielectric test. Bushings — light corrosion at flange. Cooling fans and radiators were cycling correctly under load. Grounding connections were verified intact. Inspection performed by a Substation Technician under weather conditions: ice accumulation.

SCADA alarm history for XFMR-00074 over the trailing twelve months shows 2 recorded alarms: low oil level (1), overcurrent (1). 2 of these remain unresolved.

Thermal alarm count (1) is below the capacity-upgrade-review threshold. No loading study is required at this time.

Recommended follow-up: re-inspect at the standard interval; no defects requiring intervention were found.