# Transformer Inspection Report — XFMR-00152

Asset inspection record for transformer XFMR-00152, a 10.65 MVA unit manufactured by Siemens and installed in 2018 (8 years in service). The unit is connected to feeder feeder-042-0470 at substation sub-westnatashaport-042 and its current status is de-energized.

Visual inspection findings: oil level and condition — clear, recently filtered. Bushings — light corrosion at flange. Cooling fans and radiators were operating normally with minor debris accumulation. Grounding connections were verified intact. Inspection performed by a Substation Technician under weather conditions: clear.

SCADA alarm history for XFMR-00152 over the trailing twelve months shows 2 recorded alarms: differential protection trip (1), transformer overtemperature (1). 1 of these remain unresolved.

Thermal alarm count (1) is below the capacity-upgrade-review threshold. No loading study is required at this time.

Recommended follow-up: unit is de-energized; confirm clearance and tagout status before any further work.