# Transformer Inspection Report — XFMR-00316

Asset inspection record for transformer XFMR-00316, a 41.95 MVA unit manufactured by Siemens and installed in 2014 (12 years in service). The unit is connected to feeder feeder-022-0383 at substation sub-lakemark-022 and its current status is in_service.

Visual inspection findings: oil level and condition — clear, within spec. Bushings — light corrosion at flange. Cooling fans and radiators were operating normally with minor debris accumulation. Grounding connections were verified intact. Inspection performed by a Substation Technician under weather conditions: clear.

SCADA alarm history for XFMR-00316 over the trailing twelve months shows 3 recorded alarms: breaker trip (1), communication loss (1), ground fault (1). 0 of these remain unresolved.

Thermal alarm count (0) is below the capacity-upgrade-review threshold. No loading study is required at this time.

Recommended follow-up: no action required; return to standard inspection rotation.