# Transformer Inspection Report — XFMR-00496

Asset inspection record for transformer XFMR-00496, a 46.80 MVA unit manufactured by Hitachi Energy and installed in 2023 (3 years in service). The unit is connected to feeder feeder-023-0446 at substation sub-eastlydiamouth-023 and its current status is maintenance.

Visual inspection findings: oil level and condition — darkened — schedule dielectric test. Bushings — no visible tracking. Cooling fans and radiators were operating normally with minor debris accumulation. Grounding connections were verified intact. Inspection performed by a Relay Technician under weather conditions: light rain.

SCADA alarm history for XFMR-00496 over the trailing twelve months shows 3 recorded alarms: differential protection trip (1), ground fault (1), low oil level (1). 0 of these remain unresolved.

Thermal alarm count (0) is below the capacity-upgrade-review threshold. No loading study is required at this time.

Recommended follow-up: unit is maintenance; confirm clearance and tagout status before any further work.